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	Developer Services

PO Box 3146

Cardiff

CF30 0EH
Tel:   +44 (0)800 917 2652
Fax:   +44 (0)2920 740472

E.mail: developer.services@dwrcymru.com
	Gwasanaethau Datblygu

Blwch Post 3146

Caerdydd

CF30 0EH

Ffôn:  +44 (0)800 917 2652

Ffacs:  +44 (0)2920 740472
E.bost: developer.services@dwrcymru.com



Neath and Port Talbot County Council
The Quays 

Brunel Way Baglan Energy Park

NEATH

Neath

SA11 2GG

	
	Date: 02/06/2026

	
	Our Ref: PLA0095585

	
	Your Ref: P2026/0306


Dear Sir/Madam
Grid Ref: SS772912 277384 191316

Site: Ynys Park  Cwmavon Road Cwmavon

Development: Single storey toilet block with associated drainage & fencing works

We refer to your planning consultation relating to the above site, and we can provide the following comments in respect to the proposed development. 

Firstly, with respect to the submitted application form and accompanying ‘Site Layout Plan’ (Drawing No. S002), we acknowledge that the development proposes to discharge foul and surface water flows to a septic tank and private drainage system respectively.
Since the proposal intends utilising an alternative to mains drainage for foul water, we would advise that the applicant seek advice from Natural Resources Wales and/or the Building Regulations Authority as the regulatory body for this method of drainage.[In this instance, we would advise that the development site is located immediately adjacent to a public sewerage system which is prioritised as a foul water drainage destination. Should circumstances change and a connection to the public sewerage system is preferred, we must be re-consulted on this application.
Turning to surface water drainage, as of 7th January 2019, this proposed development may be subject to Schedule 3 of the Flood and Water Management Act 2010. In the event this proposed development amounts to a total impermeable area of 100sqm or more, approval of Sustainable Drainage Systems (SuDS) features will be required in accordance with the 'Statutory standards for sustainable drainage systems – designing, constructing, operating and maintaining surface water drainage systems'. In this instance, we offer no objection to proposals for disposal of surface water flows into a private surface water system, in principle, subject to consultation and agreement with the regulatory body or riparian owner of this system.
In addition, this site is crossed by a 600mm combined public sewer with the approximate position being marked on the attached statutory public sewer record. In accordance with the Water Industry Act 1991, Dwr Cymru Welsh Water requires access to its apparatus at all times in order to carry out maintenance and repairs. Having regard to the ‘Site Layout Plan’ (Drawing No. S002), it appears the proposed development would be situated directly above the public sewer, which has a protection zone measured 3 metres either side of the centreline. Please note, the distance specified for this protection zone is indicative and based on industry standard guidelines. However, the depth of the asset will need to be verified on site which may infer a greater protection zone. For completeness, we recommend the developer refer to their title deeds to confirm if there are any covenants or restrictions associated with the asset crossing the proposed development site.
In this instance, it appears there is sufficient space and scope to re-position the development outside the protection zone of the asset. Therefore, it is strongly recommended that the proposed plans are amended to take into account the location of the asset crossing the site and we respectfully request we are re-consulted on receipt of this information. It is also recommended that the developer contact our Plan and Protect team (PlanandProtect@dwrcymru.com) to carry out a survey to verify the location of the asset and establish their relationship to the proposed development.
Accordingly, for the reasons outlined above, we offer a Holding Objection until such time as additional/amended information has been submitted and request we are re-consulted on receipt of this information.

Our response is based on the information provided by your application.  Should the proposal alter during the course of the application process we kindly request that we are re-consulted and reserve the right to make new representation.

If you have any queries please contact the undersigned on 0800 917 2652 or via email at developer.services@dwrcymru.com
Please quote our reference number in all communications and correspondence.
Yours faithfully, 
Amy Marshall
Development Planning Officer

Developer Services
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Glas Cymru Cyfyngedig




Welsh Water is owned by Glas Cymru – a ‘not-for-profit’ company.

Mae Dŵr Cymru yn eiddo i Glas Cymru – cwmni ‘nid-er-elw’.
	We welcome correspondence in

Welsh and English

Dŵr Cymru Cyf, a limited company registered in

Wales no 2366777. Registered office: Pentwyn Road,

Nelson, Treharris, Mid Glamorgan CF46 6LY
	Rydym yn croesawu gohebiaeth yn y

Gymraeg neu yn Saesneg

Dŵr Cymru Cyf, cwmni cyfyngedig wedi’i gofrestru yng

Nghymru rhif 2366777. Swyddfa gofrestredig: Heol Pentwyn

Nelson, Treharris, Morgannwg Ganol CF46 6LY.
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